## Slide 1: Facility Energy Efficiency Switch it Off - Turn it Down - Reuse it
Jon Barker CEng MEI
Chartered Energy Engineer
Enerjon
www.enerjon.co.uk

## Slide 2: Summary of Presentation
A brief overview of the basic system I use to achieve energy efficiency in any production facility.
A review of the big energy using systems found in practically all production facilities followed by actual Enerjon case study review of each.
    Heating & Ventilation (HVAC)
    Lighting
    Compressed air
    Pumps, Fans and variable speed drives
Questions

## Slide 3: Wet your appetite!
Savings can be achieved – big & small.....gas+30%
Chart: Site gas consumption KW 2008 to 2013
| Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun
2007 - 2008
2008 - 2009 | 316610 | 278513 | 272427 | 743835 | 725791 | 800980 | 1276496 | 898928 | 675908 | 710210 | 349463 | 206041
2009-2010 | 209435 | 182213 | 234914 | 448778 | 637863 | 596821 | 1288195 | 950120 | 843825 | 669747 | 529224 | 226468
2010-2011 | 212165 | 250865 | 241642 | 429621 | 662670 | 1020514 | 1297840 | 749775 | 748000 | 474262 | 290000 | 257747
2011-2012 | 247604 | 257504 | 254000 | 307988 | 408620 | 501007 | 435686 | 448855 | 335901 | 337969 | 337433 | 229226

## Slide 4
And power!.....20%
Chart: Cumulative Site Electricity Usage KWHr
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
2004 | 1683300 | 3050100 | 4916300 | 6764100 | 8624600 | 10706100 | 12731800 | 15059300 | 17126300 | 19020600 | 20928600 | 22754800
2005 | 1765000 | 3304000 | 5221000 | 6896000 | 8760000 | 10815000 | 12944000 | 15057000 | 17030000 | 18970000 | 20751000 | 21916000
2006 | 1765453 | 3404540 | 5225624 | 6959424 | 8767056 | 10628235 | 12690390 | 14630428 | 16521796 | 18347796 | 19933754 | 21203154
2007 | 1485265 | 2851939 | 4341925 | 5802222 | 7304150 | 8913474 | 10546597 | 12159177 | 13643977 | 15190077 | 16550622 | 17637522
Target | 1188212 | 2363035.1714 | 3473540 | 5221999.8 | 6573735 | 8022126.6 | 9491937.3 | 10943259.3 | 12279579.3 | 13671069.3 | 14895559.8 | 15873769.8
2008 | 1238600 | 2503445 | 3775618 | 5254810 | 6603058 | 8029644 | 9596469 | 11157874.4 | 12726485.1 | 14140720.1 | 15470651.8 | 16648284.5

## Slide 5: Where to start? 5 Steps
1. Resource & make Responsible...plan, network / get help
2. Build up the site energy picture / map
  Walk it, meters, energy surveys, data-loggers, HH data, kit consumption data, makers info, assumptions, ISO 50001....
  Where do you use your energy?
  When do you use your energy?

## Slide 6: Bank holiday - no production - check
No Production Load = 84%
Production Load
= 16%

## Slide 7
Remember 3 basic options to save energy.....
Turn off - Turn down - Reuse
3. Review your energy map & survey notes
    Identify wastes & simply categorise – low cost easy fix upto high cost hard fix.
    Identify the options that will give you the best returns & fit with site plan.

## Slide 8: Implement Improvements & Check
4. Create improvement plan and implement
  Check after changes introduced to ensure they are working to plan.
5. Repeat...Keep building the energy map for the site & repeating the improvements

## Slide 9: Energy Efficiency examples
The following examples of energy efficiency areas are similar across practically all facilities
    Lighting
    HVAC
    Compressed Air
    Steam & Hot water boilers
    Pumps & fans
    Process

## Slide 10: Lighting
Check each areas actual requirement & occupancy..... Challenge / use CIBSE guide
Compile light survey by area.....example
Explore options for high efficiency LED..... Typically saves between 50% - 90%.... +extended life / reduced maintenance.
Trial fittings / lamps until acceptable solution found......many LEDs avail, vary in light colour
Roll out across areas......Case Study

## Slide 11: HVAC
Check each area heating and ventilation actual requirements.......what do you really need? – Air change rates, % Fresh air, humidity etc
Set your HVAC to achieve what’s required.....seasonal setting!
Modern gas kit very efficient....also heat pumps and biomass to be considered - RHI
Examples – Warehouse & Packing areas

## Slide 12: Pump, Fans & VSD
Check fan and pump actual requirement.... HVAC air change etc, liquid flows....what do you really need to do?
Walk the ducts and lines.....find dampers & flow control valves.....driving with your brakes on
Investigate variable speed drive (VSD) to set flow / pressure to required and remove the brakes!!
Very small motor speed reduction required to achieve significant savings.....Case Study

## Slide 13: Compressed air
Check site requirement for pressure and dryness....what do you really need?
Do air leak survey...and fix them £££
Check compressors ability to supply to actual requirement....too big? Too small? Time / Datalog......VSD.
Multi compressors – set via sequencer
Heat recovery....90% waste.....Case Study

## Slide 14: Bottled Water - Process Wash – Energy Overview
  Each process wash uses approx 5,300 litres of water per cycle
  This requires approx 430KWH to heat up 70 Deg C per cycle.
  Steam to heat the wash water is generated in an 88% efficient Cochran fire tube boiler, with 1.5t/hr capacity.
  The steam boiler takes approx 807KWH of gas / wash cycle.
The overall process efficiency is a poor 52%
  This is mainly due to the heat required to heat up the cold boiler metal, boiler water and feed water (approx 360KWH). Zero impact of hot condensate return.
  However, process annual costs are very low as v low use process, circa £1.3k or 25% of site gas.....waste cost ic circa £600/yr.

## Slide 15: Improvement Options
+35% (310KWH) save - Install high efficiency steam generator
    By reducing boiler metal by 60% & reducing boiler water by over 75%.
    2 min heat up, circ 97% efficient.
    Cost circa £70k!....
+10% save – Turn off the boiler earlier...just before end of process wash to avoid last heat up cycle gas. Free.
+ 10% save - Investigate reducing the length of wash water flush, each 5 min reduction will reduce energy input by 10% (89KWH). Free.
1% to 2% Save, isolate off unused steam lines. Free.
Others / view report.

## Slide 16: Thanks for listening! Any Questions?
Jon Barker CEng MEI
Chartered Energy Engineer
Enerjon
www.enerjon.co.uk